OPC Servant Documentation

B. J. Hill

2021-12-10

Glossary

SBC	Single Board Computer
OPCS	OPC Servant Application
# Introduction

OPC Servant (OPCS) is a framework for providing SCADA level 0 and 1 capabilities with desktop and web HMI for configuration and monitoring.

Alternatively OpcServant can be viewed as a framework for developing OPC UA servers with desktop and web configuration interfaces.

The framework can be run headless, web based or with a desktop (touchscreen ) interface. The framework is suitable for stand alone instruments using common Single Board Computers, such as the Raspberry Pi.

The framework supports common network connectivity such as OPC UA, MQTT and SQL databases. This means OPCS based systems are easy to connect to other systems, such as Node Red and Crystal Reports. OPCS provides a basic HMI and reporting interfaces. Using packages like Node Red and Crystal Reports allows a wide range of user customisation.

OPCS is modular application written in C++ built on the wxWidgets, Wt, open62541 and open62541Cpp frameworks. WxCrafter is used to design the GUI layouts.
# Installation
OPC Servant is a Linux application. Building for Microsoft Windows and Apple Mac is expected to be possible. This how to build from sources.

Refer to the document “Raspberry Pi 4 – System Setup” for how to setup a Raspberry Pi.
## Prerequisites
### Packages Built From Sources

These are available from on GitHub. Versions in the repositories may be out of date.

- Mosquitto (https://github.com/eclipse/mosquitto.git)
- These can be cross compiled:
- Wt (https://www.webtoolkit.eu/wt)
- wxWidgets (https://www.wxwidgets.org/)
- open62541 (https://github.com/open62541/open62541.git)
- open62541cpp (git@github.com:bazza2jw/open62541Cpp.git)
- MySql++

### From Repositories

The following development packages are required:

libboost-all-dev perl libnet-ssleay-perl openssl libauthen-pam-perl
libpam-runtime libio-pty-perl python libgraphicsmagick libgraphicsmagick++
libhpdf-dev qtcreator qt5-default autoconf cmake cmake-curses-gui cmake-extras
extra-cmake-modules libsqlite3-dev sqlitebrowser minicom libmariadbclient-dev
libcjson-dev libssl-dev xsltproc libgtk3-dev libsoup-dev libsdl2-dev gstreamer-dev
libmodbus-dev apache2 libfcgi-dev
### OPC Servant Sources

Get the sources from GitHub:

https://github.com/bazza2jw/OpcServant

Build the OPCS using cmake. Qt Creator can be used as the IDE or it can be built from the command line using cmake.

## Creating the Runtime Environment
1. Create a directory /usr/local/OpcServant and make the directory writeable for the default user. Edit the cmake files to change the install directory.
2. Copy all of the files in the OpcServant/Runtime directory to this directory.
3. OPCS can now be installed with make install

## Running the application

1. Change to the installation directory (/usr/local/OpcServant)
2. Change to the bin directory
3. Run ./Servant

## udev Rules
The udev rules map USB devices so they have well known, fixed, device names.
A typical for a USB serial device is entry is:
SUBSYSTEM=="tty", ATTRS{idVendor}=="04d8", ATTRS{idProduct}=="00df",ATTRS{serial}=="0006900382" SYMLINK+="ttyFixedA"
## Local Database
All published data and process messages are written to a local SQLITE database (LOCAL.DB).
## Wt Data directory
The Wt runtime data files are in the resources directory under /usr/local/OpcServant/bin
Refer to the Wt documentation for further details.

# User Guide
## Overview
There are two user interface modes, Desktop where interface runs locally and Web where the interface runs on the target but is displayed on a web browser.
OPCS can run headless that is without a display. When running headless system configuration is done using Webmin (https://webmin.com/).
It is possible for users to interact with the display and via the web concurrently.
### Desktop Interface
#### System Properties
This form sets up the basic system parameters. This is displayed when no configuration is defined.

Site Name	This is the name of the site.
Site Password	The password to access system configuration
Enable GUI	Selects if the GUI is displayed
Enable Web	Selects if the web interface is enabled
Enable OPC	Selects if the OPC server is enabled
MainTab	This sets tab to be displayed when the system starts
OPC Port	The port to run the OPC server
OPC Namespace	The OPC namespace
Login Required	When set an username and password is required
OPC Username	The OPC username
OPC Password	The OPC password

#### User Configuration

This dialogue manages users.
New	adds a new user
Apply	saves any changes
Delete	removes a user
Enabled is checked to make a user active
Admin	is checked to make a user an administrator
#### Navigator

The navigator display on the desktop is a collection of tab panes.
##### System Tab
This configures the components.
Equipment. These are the interfaces to hardware. Right click on Equipment and select Add.
To configure an item select Properties
To delete an item select Delete
Publishers. These are interfaces to output data, and sometimes control. Right click on Equipment and select Add.

#### Reports

Reports provide tables, graphs and statistics for selected inputs and time range. The reports are generated from a local SQLITE database. Using applications such as Crystal Reports can give more comprehensive reports.
Setup Tab
Type	This selects the time range type.
Last Hour	Data is retrieved for the last hour from the time the report is run.
Last Day Data is retrieved for the last 24 hours from the time the report is run.
Last Week	Data is retrieved for the last seven days from the time the report is run.
Exact	The Start Time Start Date, End Time, End Date are specified.

Values/Alias Tab
This selects the data items that are to be read. Values are the paths to the inputs on the interfaces. Aliases are meaningful names assigned to the values. For example IN3 on an ADC module can be named Temperature_Room108.
Making Reports
After selecting the timeframe and the values/aliases click the Save button (Setup Tab).
To make the report click Make. The Table tab will have a set of tables, one for each data source.
The Graph Tab has a plot of all the values. It is best to have reports that have the save data ranges.
The Statistics Tab has a summary for each of the data sources in the report.
Printing Reports
Click on Print to print a report. Use this option to print a report in PDF format.
Export as CSV
This exports data in CSV format. After making a report the extracted data is in a SQLITE database in the report directory. This can be copied and used with report generators or other data processors.
#### Trace
This window shows diagnostic messages.
#### Item Tab Views
When an interface object has Enable Tab View set a tab is created for an assumed runtime display. This is usually current values. The System tab is for configuration.
# Web Interface
The web interface is accessed on port 8082.
There are three possible displays to access.
http://hostname:8082/admin accesses the system configuration. This is similar to the system tab on the desktop interface.
http://hostname:8082/ui accesses the interface specific tab views. This is similar to the display on the desktop.
http://hostname:8082/report selects the web based report page
Each page is password protected.

## System Configuration

## HMI

## Reports

## Maridb (MySQL) Database
A Mariadb publisher service sends published records to Mariadb SQL database.

## MQTT
### Publish
Published values are sent to the MQTT broker. The key is the path to the object value. If the object value has an alias this is used.
The data is sent as a JSON record. Node Red can be used to process and display these records.
### Commands
Messages can be received by Opc Servant. These can be mapped on commands. Typically this is used by applications such as Node Red to control outputs.
The MqttCommand class handles MQTT commands. Derive and register command handlers in a module’s plugin class.

## OPC UA
Opc Servant includes an OPC UA server based on open62541. Objects can be designed to publish values and to expose methods.
UA Expert can be used to explore the OPC UA interface. Reading and setting values and invoking methods. (see: https://www.unified-automation.com/products/development-tools/uaexpert.html)

# Programmer’s Guide
## Functional Overview
OpcServant is composed of:
1. Servant Application
2. Shared Libraries
3. Modules

The application is extended by adding modules. Modules are shared libraries with self registration embedded as part of the start up code.

The application is based, mainly, on the following libraries:

1. wxWidgets.	GUI and application framework
2. Wt	Web interface and the some signal/slot support
3. Open62451 / Open62541Cpp	OPC UA

The OpcServant application has the following threads (there may be others created by the other frameworks). These threads are created when the application starts:

1. GUI	wxWidgets desktop interface
2. Web	Wt web interface
3. OPC UA	Open652541 OPC UA
4. Data Acquisition	OpcServant classes

These threads communicate using Wt signals and slots. Typically messages are sent via the data acquisition thread. Messages are received to message queues and processed at a later time within the thread that owns the object.

## Classes
The key OpcServant classes are:
### MRL::VariantPropertyTree
This is the main data structure. Values are stored in variants in a tree.
### MRL::PropertyPath
This is the path to an object in a tree.
### MRL::ObjectManager
This is the factory for the runtime objects and the configuration and display interfaces. The key functions, that will need deriving for a given implementation are:
bool createRT(const PropertyPath &path)
Creates a runtime object.

bool edit(wxWindow *w, const PropertyPath &s)
Edits a runtime object’s configuration in the GUI.

bool edit(Wt::WWidget *w, const PropertyPath &s)
Edits a runtime object’s configuration in the web interface.

bool buildMenu(wxMenu *m, const PropertyPath &s)
Builds the context menu for an object in the GUI

bool buildMenu(Wt::WPopupMenu *m, const PropertyPath &s)
Builds the context menu for an object in the web interface

wxWindow * createTabWindow(wxWindow *parent, unsigned id)
Creates a tab window in the GUI interface for the user interface

Wt::WContainerWidget * createWebWindow( Wt::WContainerWidget *root,unsigned id);
Creates a tab window in the web interface for the user interface

There are templates for common forms:

ObjectManagerRT	A typical data collection / interface

ObjectManagerPublisher	A typical publisher

ObjectManagerI2cRT	A typical I2C interface

There is a set of standard configuration dialogues for network, serial and I2C interfaces, that can be used with these templates. Often an object manager can be defined in a single line:

typedef ObjectManagerI2cRT<BME280RT> BME280ObjectManager;

### MRL::Bobject
Base object, derived from Wt::WObject that mainly handles messages. BObject messaging is thread safe. The process() function must be called from time to time by the owning thread to action messages.
### MRL::RTObject
The run time object for interfaces and publishers. These are called in the context of the DAQ thread, unless otherwise noted.
void start();
When an object starts the object’s configuration is loaded and initialised.

void stop();
When an object stops any claimed resources are released and clean up.

void publish()
Publishing values takes place at the publish interval. Published data is passed to the publishing objects such as MQTT and SQL databases. Published data is best thought of as permanently recorded data.

void measure();
This function is called at the Measure Interval. Measured values are typically used to update displays and perform control and alarm functions.

void updateOpc(OpcServer &server, Open62541::NodeId &objectNode)
This function is invoked to update the OPC data structures. This is called from the OPC thread in response to an object update event (usually from the measure event).

void initialiseOpc(OpcServer &server, Open62541::NodeId &objectNode)
This is invoked by the OPC thread in response to an object start event. The RTObject typically makes local references to the OPC value nodes. The OPC server browser functions can be used to generate and manipulate a tree of NodeIds.

The polling functions are called periodically by the Daq object.

void process()	Called at 20 ms (approx) intervals

These functions are called at the following intervals (if enabled by the usexxx method):
void onOneSecond(time_t t)
void onOneMinute(time_t t)	-	hh:mm:00
void onOneHour(time_t t)	-	hh:00:00
void onOneDay(time_t t)	- 00:00:00
void updateObject(int state = STATES::States::StateOk, time_t timeStamp = wxDateTime::GetTimeNow())
This function is called to mark that an object has updated all of its runtime data. This generates a message that triggers user interfaces to update and the OPC server to update the data for the RTObject.

void updateValue(const T &v, const std::string & tag = VALUE_TAG, int state = STATES::States::StateOk)
This function updates one value for the object in the runtime data and generates an object value update message.

void publishValue(***)
These functions publish an object value and send an object publish message, to any publishers.

void publishRecord(***)
these functions publish a record of object data. A record is typically a JSON object that includes all the object values and meta data. It is free form.

StringVector & inputs()
This is the list of input value tags (names). These can be statically defined or dynamic.

StringVector &outputs()
This is the list of output value tags (names)

### MRL::Message
The message packet object. This is a flexible message structure (a map of variants) used to communicate between objects and threads.
### MRL::Plugin
The module self registration class. Provides the entry points to the modules. A module may define many different types of object.
        virtual void initialise();
This entry point is called on start up from the main thread to create the object managers.

        virtual void initialiseOpc();
This entry point is called by the OPC server to create the OPC Type Objects factory for each of the objects defined in the initialise() function. The association is by name.
 An OPC type object is a collection of OPC Nodes that is instantiated for each instance of a run time object.

### MRL::Common
This is a singleton that holds the global data.

## Module Developer Guide
OpcServant is extended by adding modules to the application.

There are two types of module interface and publisher.

Interface modules communicate with input / output sub systems, such as voltage inputs, relay outputs and sensor modules. Publishers send the processed data to places like SQL databases and data processors (via for example MQTT)

To develop a new module refer to the existing modules. Copying an existing module that does something similar and doing a global name change will be a large part of the required work.

Most of the work is in the runtime (RT) object periodic processing (usually as a state machine) and the configuration dialogues. The OPC type object functions usually require adapting but to a lesser extent.

The configuration dialogues are mostly getting and setting fields between the configuration object and the forms. The stock dialogues handle the common cases.

Runtime object configurations are stored as JSON records in a SQLITE database index by the object id. Objects are also held in a tree structure. Hence objects can be accessed by object id and object path. The object directory is stored as JSON as a record.

Each object has configuration data as a variant property tree and runtime data as a variant property tree. Accessing these trees is thread safe.

Generally in the periodic processing function, call down to the base class and only claim resources (file handles) while in the function. That is open on entry and close on exit this avoids contention with other objects sharing the same bus.

## Configuration Dialogues
The standard configuration dialogues are based on a tabbed container to which pages are added.

### Desktop
Desktop configuration dialogues use MRL::SetupDialog as the container

The standard dialogues are:

SetupI2cDialog
SetupSerialDialog
SetupNetworkDialog
SetupNodeSerial
SetupDatabaseDialog

### Web
Web configuration dialogues use MRL::ConfigurationWebForm as the container

The standard dialogues are:

ConfigurationI2CWebDialog
ConfigurationSerialWebDialog
ConfigurationDatabaseWebDialog
ConfigurationNetworkWebDialog
ConfigureSerialNodeWebDialog

## Runtime Interface

Runtime interfaces are added as tabs to the display. Runtime interfaces can be used to show current values and to control. In this way instrument HMIs (front panels) can be developed.

Node Red is an alternative method for web based instrument HMIs. Node Red has the advantage of being easily customisable to meet varied needs.

Each runtime display maps on to a runtime object through the runtime object identifier. References to objects should not be cached, they may change. Rather the reference to the runtime object should be obtained from the DaqCommon object (via the static function Common::daq()) when required. References are volatile.

Information is passed between the interfaces by messaging or accessing the object’s runtime data tree. The runtime data tree is thread safe for access.